# Open Geospatial Consortium Inc.

# buildingSMART alliance

Date: 02/10/09

Version: 1.0

Category: Engineering Report

AECOO-1 Testbed

bSa Project 2008-STP-01

AECOO-1 Testbed Information Delivery Manual (IDM) for Building Performance and Energy Analysis (BPEA) Thread

# Copyright notice

Copyright © 2008 US General Services Administration (GSA). All Rights Reserved.

# Warning

This document is not an OGC Standard or Specification. This document presents a discussion of technology issues considered in an Interoperability Initiative of a joint buildingSMART alliance/ OGC Interoperability Program Initiative. The content of this document is presented to create discussion in the AECOO industry on this topic; the content of this document is not to be considered an adopted specification of any kind. This document does not represent the official position of the OGC or buildingSMART alliance nor of the OGC Technical Committee or any alliance partner engaged in this Initiative. It is subject to change without notice and may not be referred to as an OGC or other standards organization’s Standard or Specification. However, the discussions in this document could very well lead to the definition of a specification or standard.

Recipients of this document are invited to submit, with their comments, notification of any relevant patent rights of which they are aware and to provide supporting documentation.

Table of Contents

1	Process Model	4

1.1	Overview	4

1.1.1	Cyclical Design	5

1.1.1.1	Conceptual	5

1.1.1.2	Detailed	5

1.2	Specification of Process	6

1.2.1	Concept Design Phase Energy Analysis	6

1.2.1.1	Concept Design BIM Complete	7

1.2.1.2	Prepare/Adjust BIM for Energy Analysis [1.1]	7

1.2.1.3	Export BIM for Analysis [1.2]	7

1.2.1.4	Analyze Energy Demand and Consumption [1.3]	8

1.2.1.5	Review Energy Analysis Results [1.4]	8

1.2.1.6	Prepare Submission for Review/Approval [1.5]	9

1.2.1.7	Validate BIM for Energy Analysis [1.6]	9

1.2.1.8	Analyze Energy Demand and Consumption [1.7]	9

1.2.1.9	Review Energy Analysis Results [1.8]	9

1.2.1.10	Prepare Analysis Report [1.9]	9

1.2.1.11	Evaluate Energy Performance, Operating Costs, Capital Costs [1.10]	10

1.2.1.12	Prepare Design Feedback [1.11]	10

1.2.2	Prepare/Adjust BIM for Energy Analysis	10

1.2.2.1	Create Project Space Types [1.1.1]	11

1.2.2.2	Assign Space Types to Occurrences [1.2.3]	11

1.2.2.3	Customize/Extend Space Type Data [1.1.4]	11

1.2.2.4	Zone Spaces [1.1.4]	12

1.2.2.5	Assign Energy Targets [1.1.5]	13

1.2.2.6	Customize/Extend Energy Targets [1.1.6]	13

1.2.2.7	Modify Building Design/Geometry [1.1.7]	13

1.2.2.8	Create Project Construction Types [1.1.8]	14

1.2.2.9	Assign Construction Types to Occurrences [1.1.9]	14

1.2.2.10	Customize/Extend Construction Type Data [1.1.10]	14

1.2.2.11	Validate BIM for Energy Analysis [1.1.11]	15

1.3	Specification of Data Objects	15

1.3.1.1	Industry Construction Type Library	15

1.3.1.2	Project Construction Type Library	15

1.3.1.3	Industry Space Type Library	15

1.3.1.4	Project Space Type Library	15

1.3.1.5	Energy Target	16

1.3.1.6	Mechanical System Library	16

1.3.1.7	Analysis Method	16

1.3.1.8	Energy Tariff	16

1.3.1.9	Weather Data Library	16

1.3.2	Exchange Requirement Data Objects	17

1.3.2.1	ER_EnergyAnalysis_Inputs_1	17

1.3.2.2	ER_EnergyAnalysis_Inputs_2	17

1.3.2.3	ER_EnergyAnalysis_Results	17

1.4	Specification of Decision Point Gateways	17

1.4.1.1	Ready for Simulation	17

1.4.1.2	Valid Energy Analysis BIM?	17

1.4.1.3	Results Acceptable?	18

1.4.1.4	Perform Client Energy Analysis?	18

1.4.1.5	Results Complete per Client Request?	18

1.4.1.6	Energy Performance Accepted?	18

2	Exchange Requirements for Energy Simulation Input	19

2.1	Overview	20

2.2	Exchange Requirements - Energy Analysis Inputs 1 (Architect)	21

2.3	Exchange Requirements - Energy Analysis Inputs 2 (Mechanical Engineer/Energy Consultant)	24

3	Exchange Requirements for Energy Simulation Results	28

3.1	Overview	29

3.2	Exchange Requirements - Energy Analysis Results	30

# Process Model

| Name | OGC – Energy Analysis at Concept Design Phase |
| --- | --- |

| Change Log |
| --- |
| 15-May-08 | Initial creation, adapted from Energy Analysis IDM originally developed by Jeff Wix for buildingSMART Norway | Richard See |
| 05-Jun-08 | Changes for version 0.15 | Richard See |
| 27-Aug-08 | Changes for version 0.2 | Benjamin Welle Richard See |
| 3-Sep-08 | Changes for version 0.3 | Benjamin Welle Richard See |
| 2-Dec-08 | Changes for version 0.9 | Benjamin Welle Richard See |
| 18-Jan-09 | Changes for version 0.95 | Benjamin Welle Richard See |
| 04-Feb-09 | Final changes for version 1.0 | Benjamin Welle Richard See |

## Overview

Energy analysis is concerned with predicting the usage profile and cost of energy consumption within buildings. Conceptual design phase energy modeling is used to provide the design team with first order of magnitude feedback about the impact of various building configurations on annual energy performance. Conceptual phase energy modeling requires the designer to make assumptions for a wide of range of simulation input if information is not yet available. It takes into account as input data:

building geometry including the layout and configuration of spaces,

building orientation,

building construction including the thermal properties of all construction elements including walls, floors, roofs/ceilings, windows, doors, and shading devices,

building usage including functional use,

internal loads and schedules for lighting, occupants, and equipment,

heating, ventilating, and air conditioning (HVAC) system type and operating characteristics,

space conditioning requirements,

utility rates,

weather data,

The output results of energy analysis may include:

assessment of the space and building energy performance for compliance with regulations and targets,

overall estimate of the energy use by space and for the building and an overall estimate of the energy cost,

time based simulation of the energy use of the building and time based estimate of utility costs,

lifecycle estimate of the energy use and cost for the building,

For the purposes of this process map, conceptual phase energy analysis is considered to include the assessment of heating and cooling demand within a building during peak periods.

Various types of analyses are within the scope of this process map, including:

setting comfort criteria for spaces including minimum and maximum required indoor air temperatures (summer and winter), minimum fresh air requirements,

heat loss/gain calculations using well defined analytical methods,

energy performance rating system and/or energy code requirement compliance,

analysis of energy consumption in meeting the building energy demands,

optimization of energy performance related to equipment or system type and related equipment/system performance characteristics considering lifecycle cost, environmental impact issues, and comfort aspects.

### Cyclical Design

The process of developing energy analysis throughout the design stages of a project is considered to be divided into 2 key parts:

#### Conceptual

This is the analysis work undertaken during the programming and concept design stage of the project. It is about providing advice on the potential energy performance of a building and its systems to other design roles. The aim of this analysis is to have an impact on the overall building design, determine the feasibility of concepts in an energy context and to establish energy targets. Conceptual analysis may be undertaken in the absence of detailed geometric information about the building layout, though frequently general spatial layout is included during this stage. The designer is more concerned with relative performance values between the design options being considered, rather than absolute performance values.  Though assumptions typically must be made at this stage, maintaining consistent assumptions between the options being evaluated allows for relative performance to be evaluated.

#### Detailed

This is the analysis work undertaken during the schematic and design development stages of the project and assumes the availability of geometric and building system information for the design. The overall process is the same at each stage of work, the difference being simply about the extent of the information available and the level of certainty that can be applied to the information. These factors impact the analysis methods used, which may range from relatively simple at the earlier design stages to detailed dynamic simulations at the later design stages.

Within this process map, the conceptual design phase of the project is shown.

## Specification of Process

### Concept Design Phase Energy Analysis

#### Concept Design BIM Complete

| Type | Initial Concept BIM |
| --- | --- |
| Documentation | It is assumed at this point the architect has defined a building concept design complete with all the required building elements and space objects. This design provides a proposed building layout including functional and non-functional space configuration and placement of other geometric elements. Non-functional spaces such as technical spaces, circulation spaces, shafts, etc. must be defined by a space objects and not left as unidentifiable voids surrounded by geometry. Spaces that represent multi-story spaces such as atria and vertical distribution routes such as shafts, stairways and elevator shafts should be represented as distinct spaces at each level of the building that are related to each other vertically (either via an opening in a slab or an element located at the opening for e.g. safety purposes). The Concept Design BIM should include: the site and building location the building orientation including its relationship to true north the site and building elevation above a reference datum the building story information 3D geometry of adjacent buildings 3D geometry of the building, including walls (exterior/interior), curtain walls, roofs, floors/slabs, ceilings, windows/skylights, doors, and shading devices space objects, including those defined by virtual space boundaries At the end of this task, the following exchange requirements from ER Energy Analysis Inputs 1 should be met: Project, Site, Site Context, Building, and Building Stories. The following exchange requirements from ER Energy Analysis Inputs 1 should be partially met: Spaces and Building Elements (General). |

#### Prepare/Adjust BIM for Energy Analysis [1.1]

| Type | Sub-Process |
| --- | --- |
| Documentation | At this point, the Concept Design BIM is passed to the appropriate designer to prepare the BIM for energy analysis. The designer may still be the architect, a mechanical engineer or energy consultant, or any combination of those three. Details of this sub-process are described in Section 1.2.2. |

#### Export BIM for Analysis [1.2]

| Type | Task |
| --- | --- |
| Documentation | Once the BIM has been prepared for energy analysis and validated in Task 1.1, it is exported to IFC for energy simulation. At this point, all the required exchange requirements in ER Energy Analysis Inputs 2 have been met. Prior to being able to use the IFC file for energy analysis, there may need to be some additional data reduction/transformation steps that need to take place. One approach is to use a series of preprocessors or middleware to make these changes, such as LBNL’s Geometry Simplification Tool (GST), IDF Generator, and/or IDF Editor. This sequence of tools enables the designer to convert the IFC information into an input file for energy simulation, in this case EnergyPlus. In the future, such a sequence of steps may be combined into a single “Import IFC” function that building performance software vendors may implement. |

#### Analyze Energy Demand and Consumption [1.3]

| Type | Task |
| --- | --- |
| Documentation | The designer is now almost ready to perform an energy analysis. After selecting the appropriate utility/energy tariff data, weather data, and analysis method, the simulation is run. The energy analysis will determine the energy demand (peak load) for the building in addition to the annual energy consumption. Energy Demand Energy demand is the heating and/or cooling load that may be used for the purposes of HVAC system sizing. It represents the maximum thermal load on the building for the specified design days for the winter and/or cooling season. Energy demand will be determined for each zone and the total demand obtained for the building (or parts of the building) by aggregating the zone peak loads for the specified design hour. Zone peak loads may or may not occur at the same as the building peak load. Energy demand will be determined based on the proposed building space layout, proposed construction types assigned to building elements, HVAC system, infiltration, outside air requirements, internal loads from people, lighting and equipment, and the operating schedules for occupancy, lighting, equipment, and HVAC. The designer must be cautious when evaluating simulation results, for the peak loads as determined for the specified design day may not necessarily end up being the peak loads the building experiences throughout the year. When this is the case, the user will most likely find that many of the spaces cannot maintain the required temperature setpoints for some period of the year. In energy simulation engines, this inability to maintain the required operating setpoints in the space usually is represented as the number of hours for a particular zone that fall outside of the specified temperature range, and this metric is frequently used as a measure of thermal comfort. Annual Energy Consumption Annual energy consumption is the energy used every year for heating, cooling, lighting, and equipment the building. Energy consumption may be determined for each space, zone, and/or as a total consumption for the building (or parts of the building). If energy consumption data is only calculated on the zone level, it may not be possible to determine individual space profiles within that zone. |

#### Review Energy Analysis Results [1.4]

| Type | Task |
| --- | --- |
| Documentation | The results of the energy simulation are obtained and evaluated. At this point, all the exchange requirements of the ER Energy Analysis Results should be met. The results may be evaluated directly from the energy simulation output, or the results may be checked using a BIM model checker using the IFC file with the results written back to it. Regardless of the chosen method, the results are compared to the energy targets set forth for the project. If the targets are not achieved, then the designer must go back to Task 1.1 and make further modifications to the building geometry, constructions, or some other building design variable. If the targets are achieved, the designer can move forward to Task 1.5. It is frequently the situation where the designer is evaluating a given design not just against its energy performance, but also against other performance targets such as first cost, circulation efficiency, etc. If a design meets the energy targets, but falls short of first cost targets, for example, and vice versa, then the design can be “failed” and designer will have to further iterate on the building design by returning to Task 1.1. |

#### Prepare Submission for Review/Approval [1.5]

| Type | Task |
| --- | --- |
| Documentation | Once the designer is satisfied with a design, they will prepare a submission package for client review/approval. |

#### Validate BIM for Energy Analysis [1.6]

| Type | Task |
| --- | --- |
| Documentation | After receipt of the IFC BIM complete with ER Energy Analysis Inputs 2 and ER Energy Analysis Results, the client will use a data validation tool to verify that the BIM meets the requirement of the MVD. |

#### Analyze Energy Demand and Consumption [1.7]

| Type | Task |
| --- | --- |
| Documentation | The client may use internal staff or hire an outside consultant to verify the designer’s energy simulation results. After selecting the appropriate utility/tariff data, weather data, and analysis method, the simulation is run. The energy analysis will determine the energy demand (peak load) for the building in addition to the annual energy consumption. Details on energy demand and annual energy consumption can be found in Task 1.3. |

#### Review Energy Analysis Results [1.8]

| Type | Task |
| --- | --- |
| Documentation | The results of the client energy simulation are obtained and evaluated. The results are reviewed to ensure accuracy and integrity. |

#### Prepare Analysis Report [1.9]

| Type | Task |
| --- | --- |
| Documentation | Once the client simulation results are verified and approved, and analysis report is prepared comparing the results of the client simulation with those of the designer. |

#### Evaluate Energy Performance, Operating Costs, Capital Costs [1.10]

| Type | Task |
| --- | --- |
| Documentation | The client will evaluate the analysis report submitted by their internal staff or consultant. Energy performance, operating costs, and capital costs (in addition to any other building program requirements) will be evaluated, resulting in a "go/no go" decision for the design. |

#### Prepare Design Feedback [1.11]

| Type | Task |
| --- | --- |
| Documentation | The client will document the resulting energy analysis (which may or may not include an independent energy analysis for comparison/validation), projections, and recommendations for the design team. The design feedback package will be delivered back to the designer, and will include either an approval or rejection of the design originally submitted to the client by the designer. If the client performed an independent energy analysis and the design is rejected, the client will submit the new IFC file with the revised ER Energy Analysis Results back to the designer. |

### Prepare/Adjust BIM for Energy Analysis

#### Create Project Space Types [1.1.1]

| Type | Task |
| --- | --- |
| Documentation | This process considers that an industry space type data library exists from which a project specific space type library can be derived. The space type selected drives assumptions for thermal performance characteristic of the space for energy simulation. The industry space type library may come from a variety of sources, including ASHRAE 90.1, ASHRAE 62.1, CA Title 24, or the IEEC. The industry space type library may be accessed from a server over the web or from directly within the BIM-authoring application. The project specific space type library contains only definitions of those space types that can be used on the project of concern. Space types that drive thermal simulation assumptions may also reference other classification systems, such as Omniclass. A single space object may have one, two, three, or more space types assigned to it based on the needs of the client. Multiple on-going projects between the GSA, Construction Specification Institute (CSI), the International Code Council (ICC), and others are working to map various naming classifications systems to each other. When this work is complete, consistent and transparent mapping of space names within BIM models will be possible. Project space data is expected to provide most of the following: space type name outside air requirements internal loads for lighting, occupants, and equipment space conditioning requirements operating schedules for lighting, occupants, and equipment The default assumptions based on the project space type is meant to be a starting point only, and the values may be modified prior to running the simulation. |

#### Assign Space Types to Occurrences [1.2.3]

| Type | Task |
| --- | --- |
| Documentation | Once the project space type library has been created, the designer may assign the space types to space occurrences, making a connection between the space occurrence and the type of space to which it conforms. |

#### Customize/Extend Space Type Data [1.1.4]

| Type | Task |
| --- | --- |
| Documentation | This task deals with individual spaces that may not be fully defined within the project space type library, or not defined to the designer’s satisfaction. Initial data may be taken from a library template but is then updated (or added) for the particular space being dealt with. Upon completion, information about this space may be saved back to the project space type library for future application. Examples include the designer wanting to lower a default ASHRAE value for interior lighting intensity because he/she wants to be more aggressive to meet LEED certification requirements, or adding a lighting schedule because the default space data from the industry standard space type library did not include one. At the end of this task, the following exchange requirements from ER Energy Analysis Inputs 1 and 2 should be met: Project, Site, Site Context, Building, Building Stories, Spaces, Spaces (Thermal Comfort Criteria), Spaces (Ventilation Criteria), and Spaces (Ventilation Design). The following exchange requirements from ER Energy Analysis Inputs 1 and 2 should be partially met: Building Elements (General). |

#### Zone Spaces [1.1.4]

| Type | Task |
| --- | --- |
| Documentation | At the heart of any energy simulation is the concept of a thermal zone. A thermal zone is a single space or group of indoor spaces that has uniform thermal load profiles and conditioning requirements. A simple way to think of a thermal zone is as a space that can effectively be conditioned using only one thermostat. Thermal zoning of a building helps the engineer determine the number and type of HVAC systems required. However, defining thermal zones requires a certain amount of engineering judgment. For example, perimeter offices all facing a similar orientation (N, S, E, W), could logically be combined into one thermal zone since the solar, occupancy, lighting, and equipment loads are all similar amongst all the offices. However, differences in personal thermal comfort may make it more prudent for the engineer to zone the offices into multiple thermal zones so that the occupants have more individual control over their environment. Strategies for thermal zoning can differ significantly by building type. For example, hotels frequently have multi-perimeter and core thermal zones due to the wide range of thermal conditions (e.g. some people like it warm, some like it cool). Small residences typically have only one conditioned thermal zone (one thermostat), plus unconditioned spaces such as unconditioned garages, attics, and crawlspaces, and unconditioned basements. When a designer “zones” spaces, he/she groups together individual spaces with similar thermal profiles and conditioning requirements into a single thermal zone. This thermal zone is typically served by a single HVAC system, though a single HVAC system can serve more than one thermal zone. Thermal zones need not contain contiguous spaces, an example being the creation of a single thermal zone for all the bathrooms in a building, despite there being bathrooms on multiple floors. Spaces are zoned in BIM-authoring applications in different ways, including drawing zone boundaries, picking spaces objects, and dragging and dropping spaces objects into zone objects. Included in this task is the assignment of the following zone information: zone type zone conditioning requirement HVAC type HVAC schedule infiltration rate daylighting data At the end of this task, the following exchange requirements from ER Energy Analysis Inputs 1 and 2 should be met: Project, Site, Site Context, Building, and Building Stories, Spaces, Spaces (Thermal Comfort Criteria), Spaces (Ventilation Criteria), Spaces (Ventilation Design), and Energy Analysis Zones. The following exchange requirements from ER Energy Analysis Inputs 1 and 2 should be partially met: Building Elements (General). |

#### Assign Energy Targets [1.1.5]

| Type | Task |
| --- | --- |
| Documentation | This process considers that an industry energy target data library exists from which data can be extracted and assigned to the building model. Energy target data provides metrics for energy performance goals. Possible units include: Btu/ft2, kWh/person, kWh/ft2 cooling, kWh/ft2 heating, kWh/ft2 by end use, etc. Targets may be based on ASHRAE 90.1, state or local codes, LEED requirements, or some other source. The default assumptions based on the energy target source data is meant to be a starting point only, and the values may be modified prior to running the simulation. |

#### Customize/Extend Energy Targets [1.1.6]

| Type | Task |
| --- | --- |
| Documentation | In this task the engineer or consultant modifies or adds data for energy targets. Initial data may be taken from a library template but is then updated (or added) for the particular building being modeled. At the end of this task, the following exchange requirements from ER Energy Analysis Inputs 1 and 2 should be met: Project, Site, Site Context, Building, Building (Energy Target), Building Stories, Spaces, Spaces (Thermal Comfort Criteria), Spaces (Ventilation Criteria), Spaces (Ventilation Design), and Energy Analysis Zones. The following exchange requirements from ER Energy Analysis Inputs 1 and 2 should be partially met: Building Elements (General). |

#### Modify Building Design/Geometry [1.1.7]

| Type | Task |
| --- | --- |
| Documentation | In this step, the designer makes any necessary modifications to the building geometry or any other building design parameter other than those addressed by project construction or space types. At the end of this task, the following exchange requirements from ER Energy Analysis Inputs 1 and 2 should be met: Project, Site, Site (Outside Design Criteria), Site Context, Building, Building (Energy Target), Building Stories, Spaces, Spaces (Thermal Comfort Criteria), Spaces (Ventilation Criteria), Spaces (Ventilation Design), Energy Analysis Zones, and Photovoltaics. The following exchange requirements from ER Energy Analysis Inputs 1 and 2 should be partially met: Building Elements (General). |

#### Create Project Construction Types [1.1.8]

| Type | Task |
| --- | --- |
| Documentation | This process considers that an industry construction type data library exists from which a project specific construction type library can be derived. The construction type selected for a building element significantly impacts the thermal performance of that element, based on the construction R-value, reflectance, transmittance, and thermal mass effects. The industry construction type library may come from a variety of sources, including the ASHRAE Fundamentals, ASHRAE 90.1, CA Title 24, and the IEEC. The industry construction type library may be accessed from a server over the web or from directly within the BIM-authoring application. The project specific construction type library contains only definitions of those construction types that can be used on the project of concern. Construction types that drive thermal simulation assumptions may also reference other classification systems, such as Omniclass. A single construction object may have one, two, three, or more construction types assigned to it based on the needs of the client Project construction data is expected to provide most of the following: construction type name material layer sequence for the construction material layer thermal properties overall thermal properties of the construction The default assumptions based on the project construction type is meant to be a starting point only, and the values may be modified prior to running the simulation. |

#### Assign Construction Types to Occurrences [1.1.9]

| Type | Task |
| --- | --- |
| Documentation | Once the project space type library has been created, the designer may assign the construction types to building element occurrences, making a connection between the building element occurrence and the type of construction to which it conforms. |

#### Customize/Extend Construction Type Data [1.1.10]

| Type | Task |
| --- | --- |
| Documentation | This task deals with individual constructions that may not be fully defined within the project construction type library, or not defined to the designer’s satisfaction. Initial data may be taken from a library template but is then updated (or added) for the particular space being dealt with. Upon completion, information about this construction may be saved back to the project construction type library for future application. At the end of this task, the following exchange requirements from ER Energy Analysis Inputs 1 and 2 should be met: Project, Site, Site Context, Building, Building (Energy Target), Building Stories, Spaces, Spaces (Thermal Comfort Criteria), Spaces (Ventilation Criteria), Spaces (Ventilation Design), Building Elements (General), Building Elements (Opaque and Glazing), Material (Opaque), Material Layer (Opaque), Material Layer Set (Opaque), and Energy Analysis Zones. |

#### Validate BIM for Energy Analysis [1.1.11]

| Type | Task |
| --- | --- |
| Documentation | After geometry, construction type, space type, and any other modifications to the building are made, the BIM is ready to be validated for energy analysis. Validation will take place by exporting an IFC file and using a model checker to ensure the MVD requirements have been met. The IFC file will contain 2nd level space boundaries, which define the heat transfer surfaces required for energy simulation. Space boundaries relate spaces and building elements. This is preferably done automatically by the BIM-authoring application, though it may be done by other means such as via a middleware. |

## Specification of Data Objects

#### Industry Construction Type Library

| Type | Data Object |
| --- | --- |
| Documentation | The industry construction type data library provides information that drives assumptions for the thermal performance characteristics of constructions for energy simulation. The industry construction type library may come from a variety of sources, including the ASHRAE Fundamentals, ASHRAE 90.1, CA Title 24, and the IEEC. The industry construction type library may be accessed from a server over the web or from directly within the BIM-authoring application. |

#### Project Construction Type Library

| Type | Data Object |
| --- | --- |
| Documentation | The project construction type data library is derived for the project from the industry construction type library, and reflects any modifications or additions the designer has made to the industry source data. |

#### Industry Space Type Library

| Type | Data Object |
| --- | --- |
| Documentation | The industry space type data library provides information that drives assumptions for the thermal performance characteristics of spaces for energy simulation. The industry space type library may come from a variety of sources, including ASHRAE 90.1, ASHRAE 62.1, CA Title 24, or the IEEC. The industry space type library may be accessed from a server over the web or from directly within the BIM-authoring application. |

#### Project Space Type Library

| Type | Data Object |
| --- | --- |
| Documentation | The project space type data library is derived for the project from the industry space type library, and reflects any modifications or additions the designer has made to the industry source data. |

#### Energy Target

| Type | Data Object |
| --- | --- |
| Documentation | Energy target data provides metrics for energy performance goals. Possible units include: Btu/ft2, kWh/person, kWh/ft2 cooling, kWh/ft2 heating, kWh/ft2 by end use, etc. Targets may be based on ASHRAE 90.1, state or local codes, LEED requirements, or some other source. |

#### Mechanical System Library

| Type | Data Object |
| --- | --- |
| Documentation | The mechanical system library contains a variety of HVAC system types that the user may assign to zones in the BIM model. HVAC system type definitions may come from a wide variety of sources, including ASHRAE 90.1, Title 24, or EnergyPlus/DOE-2 libraries. |

#### Analysis Method

| Type | Data Object |
| --- | --- |
| Documentation | Select the method of analysis that is to be used during this stage of work. The method must be consistent with data that is available. The analysis method used refers to the thermal simulation engine or software interface selected for analysis (e.g. EnergyPlus, DOE-2, eQUEST, IES, etc.). |

#### Energy Tariff

| Type | Data Object |
| --- | --- |
| Documentation | Identifies the cost values that apply to the source of energy and its form of usage. During the early stages of design, information may be obtained from similar projects. As design progresses, information is obtained from the energy source provider. The tariff may be applicable not only to the energy source but also to when the energy source is used. For instance, electrical energy may carry a lower tariff when it is used in 'off peak' situations since such this may be useful to the source provider in load balancing. |

#### Weather Data Library

| Type | Data Object |
| --- | --- |
| Documentation | The weather data object provides annual (8760) weather data for use in the energy simulation. The source data for these weather data files varies, including data from Typical Meteorological Year (TMY, TMY2, TMY3), Weather Year for Energy Calculations (WYEC2), and International Weather for Energy Calculations format from ASHRAE (IWEC). Data file formats include EnergyPlus Weather Data (EPW) as well as ESP-r, DOE-2 and BLAST weather text format files. Some of the information that these files include is the following: external temperature and humidity solar radiation wind speed wind direction It is assumed that the weather data library provides any additional outside design criteria that is required. The outside design criteria drive the calculation of peak loads and HVAC equipment sizing, and may come from sources such as ASHRAE. |

### Exchange Requirement Data Objects

#### ER_EnergyAnalysis_Inputs_1

| Type | Data Object |
| --- | --- |
| Name | ER_EnergyAnalysis_Inputs_1 |
| Documentation | Exchange of partial set of energy simulation input information for peak load sizing and annual energy consumption calculations. This data exchange requirement is completed by the architect. |

#### ER_EnergyAnalysis_Inputs_2

| Type | Data Object |
| --- | --- |
| Name | ER_EnergyAnalysis_Inputs_2 |
| Documentation | Exchange of complete set of energy simulation input information for peak load sizing and annual energy consumption calculations. This data exchange requirement is completed by the mechanical engineer and/or energy consultant. |

#### ER_EnergyAnalysis_Results

| Type | Data Object |
| --- | --- |
| Name | ER_EnergyAnalysis_Results |
| Documentation | Exchange of complete set of energy simulation output information including comfort metrics, peak load information, annual energy consumption, and utility rate information. |

## Specification of Decision Point Gateways

#### Ready for Simulation

| Type | Decision Point |
| --- | --- |
| Documentation | At this point the designer must decide if all the desired design changes have been made and the model is ready for energy simulation. If so, the model is ready for simulation. If not, the designer must further modify the building design. |

#### Valid Energy Analysis BIM?

| Type | Decision Point |
| --- | --- |
| Documentation | After deciding that the model is ready for simulation, the designer uses a model checker to ensure that all the input exchange requirements have been met. This step also takes place when the client evaluates the BIM model submitted to them by the designer. If the BIM model meets the requirements set forth by the rule checking sets in the model checker, the BIM is valid. If not, it is invalid. |

#### Results Acceptable?

| Type | Decision Point |
| --- | --- |
| Documentation | The designer evaluates the results of the energy simulation and compares them to the energy targets for the design. If the design meets the energy targets, as well as any other project performance metrics (such as first cost), the results are acceptable. If not, the designer must further modify the building design. |

#### Perform Client Energy Analysis?

| Type | Decision Point |
| --- | --- |
| Documentation | The client may want to perform an independent energy analysis to validate the results of the designer’s analysis. This independent energy analysis may be executed by internal staff of the client, or by a consultant. |

#### Results Complete per Client Request?

| Type | Decision Point |
| --- | --- |
| Documentation | The internal staff or consultant that is conducting the independent energy analysis decides of the results of their analysis are accurate and reliable, and conform to the client’s work order. |

#### Energy Performance Accepted?

| Type | Decision Point |
| --- | --- |
| Documentation | The designer reviews the design feedback from the client for design approval or rejection. |

# Exchange Requirements for Energy Simulation Input

| Name | Exchange of Energy Simulation Input Parameters |
| --- | --- |

| Identifier | ER_EnergyAnalysis_Inputs_1 and ER_EnergyAnalysis_Inputs_2 |
| --- | --- |

| Change Log |
| --- |
| 15-May-08 | Initial version, adapted from Energy Analysis IDM originally developed by Jeff Wix for buildingSMART Norway | Richard See |
| 05-Jun-08 | Changes for version 0.15 | Richard See |
| 27-Aug-08 | Changes for version 0.2 | Benjamin Welle Richard See |
| 07-Sept-08 | Changes for version 0.3 | Benjamin Welle Richard See |
| 11-Sept-08 | Changes for version 0.4 | Benjamin Welle Richard See |
| 12-Nov-08 | Changes for version 0.8 | Benjamin Welle Richard See |
| 04-Dec-08 | Changes for version 0.91 | Benjamin Welle Richard See |
| 18-Jan-09 | Changes for version 0.95 | Benjamin Welle Richard See |

| Project Stage | 0 | Portfolio requirements |  |
| --- | --- | --- | --- |
|  | 1 | Conception of need |  |
|  | 2 | Outline feasibility |  |
|  | 3 | Substantive feasibility |  |
|  | 4 | Outline conceptual design | ( |
|  | 5 | Full conceptual design | ( |
|  | 6 | Coordinated design and procurement |  |
|  | 7 | Production information |  |
|  | 8 | Construction |  |
|  | 9 | Operation and maintenance |  |
|  | 10 | Disposal |  |

## Overview

The scope of this exchange requirement is the exchange of information about spaces with associated energy information and about proposed energy analysis zones. The purpose of the exchange requirement is to support the coordination of energy analysis requirements with general zoning and spacing requirements.

The exchange requirement assumes that a building model is available from which relevant geometric information required for energy analysis can be derived. It is anticipated that the building model will provide context information about the project including units to be used, coordinate systems to be adopted and the direction of true north.

The building model will provide specific information about:

the building, its location, composition, overall shape and orientation

the shape and location of adjacent buildings to enable shading effects to be determined

building stories within the building

spatial configuration

Information that is provided by this exchange requirement to enhance the initial set of building model information includes:

space type and function identification with type data being obtained from a project space type library (which is in turn derived from an industry space type library). This data will drive assumptions on internal loads, conditioning requirements, etc.

building elements construction type data with type data being obtained from a project construction type library (which is in turn derived from a industry construction type library). This data will provide information on the thermal characteristics of the building envelope and internal constructions.

space boundaries that define the relation between spaces and building elements and the geometry that describes the space boundary connection

energy targets

HVAC zoning, daylighting, and the use of photovoltaics

## Exchange Requirements - Energy Analysis Inputs 1 (Architect)

| Type of Information | Information Needed | Required | Optional | Data Type | Units |
| --- | --- | --- | --- | --- | --- |
| Project | The following properties should be included: |  |  |  |  |
|  | Identification | X |  | String | n/a |
|  | Owner/Client information |  | X | String | n/a |
|  | Model Author |  | X | String | n/a |
| Site | The following properties should be included: |  |  |  |  |
|  | Address |  | X | String | n/a |
|  | Global Coordinates | X |  | (2) triples | deg/min/sec |
|  | Site Elevation (datum)(relative to sea level) | X |  | Real | m |
|  | 2D Geometry |  | X | IFC Geometry | varies |
|  | 3D Geometry |  | X | IFC Geometry | varies |
| Site Context | The following properties should be included for existing buildings adjacent to the subject building: |  |  |  |  |
|  | Identification | X |  | String | n/a |
|  | 3D Geometry | X |  | IFC Geometry | m |
| Building | The following properties should be included (if not known then probable values should be used): |  |  |  |  |
|  | Identification | X |  | String | n/a |
|  | Global Coordinates | X |  | (2) triples | deg/min/sec |
|  | Functional Classification (OmniClass) |  | X | String | n/a |
|  | Orientation (deviation of building grid from true north, clockwise) | X |  | Real | Angular Degrees |
|  | Elevation (relative to the site datum) | X |  | Real | m |
| Building (Energy Target) | The following properties should be included (if not known then probable values should be used): |  |  |  |  |
|  | Energy Target Units (mandatory if Energy Target Value is included) |  | X | String | varies |
|  | Energy Target Value |  | X | Real | varies |
| Building Stories | The following properties should be included (if not known then probable values should be used): |  |  |  |  |
|  | Identification | X |  | String | n/a |
|  | Elevation (relative to building datum) | X |  | Real | m |
| Spaces | The following properties should be included (if not known then probable values should be used): |  |  |  |  |
|  | Identification | X |  | String | n/a |
|  | Description |  | X | String | n/a |
|  | Functional Classification - OmniClass Table 13 (reference to a classification -- see below) |  | X | Relationship | n/a |
|  | Functional Classification – Client Space Type (reference to a classification -- see below) | X |  | Relationship | n/a |
|  | Inside or Outside space | X |  | Boolean |  |
|  | Space Usage (thermal simulation type) |  | X | Enumeration value | n/a |
|  | 2D Geometry |  | X | IFC Geometry | varies |
|  | 3D Geometry | X |  | IFC Geometry | varies |
|  | Links to Space Boundaries | X |  | List of Relationships | n/a |
|  | Space Conditioning Requirement (heated and cooled, heated only, cooled only, unconditioned) |  | X | Enumeration value | n/a |
| Second Level Space Boundaries | The following properties should be included for 2nd level space boundaries: |  |  |  |  |
|  | Space Boundary Type (1=internal, 2=external, 3=virtual) | X |  | Enum | n/a |
|  | Space Boundary Tag (2nd level, “face”) | X |  | String | n/a |
|  | 3D planar geometry | X |  | IFC Geometry | m |
|  | Link to Space | X |  | Relationship | n/a |
|  | Link to Building Element | X |  | Relationship | n/a |
| Building Elements (General) | The following properties should be included (if not known then probable values should be used): |  |  |  |  |
|  | Building Element Type (wall (exterior/interior), curtain wall, roof, floor, ceiling, window, door, shading device) | X |  | Enum | n/a |
|  | Construction type (e.g. wall type, door type, window type, shading device type, etc.) Window constructions from Window 6, opaque constructions from ASHRAE Fundamentals. | X |  | String | n/a |
|  | Classification - UniFormat (reference to a classification -- see below) |  | X | String | n/a |
|  | 3D Geometry | X |  | IFC Geometry | varies |
|  | Exterior or Interior Element (i.e. Is Exterior) | X |  | Boolean | n/a |
|  | Link to Space Boundary | X |  | Relationship | n/a |
| Building Elements (Opaque- Wall, Roof, Floor, Ceiling, Door) | Added to the list above, the following properties should be included for opaque building elements (e.g. walls, floors, ceilings, roofs, doors, etc.): |  |  |  |  |
|  | Link to Material Layer Set | X |  | String | n/a |
| Building Elements (Glazing- Curtain Wall, Glazed door, Skylight, Window) | Added to the Building Elements list above, assigns thermal information to building elements to enable energy analysis. The following properties should be included for glazed building elements (e.g. windows, curtain walls, glazed doors, and skylights): |  |  |  |  |
|  | Window Assembly Exterior Surface Color of Glass (clear, bronze, silver, gold, copper, blue, green, gray, mirror) |  | X | Enum | n/a |
|  | Window Assembly Interior Surface Color of Glass (clear, bronze, silver, gold, copper, blue, green, gray, mirror) |  | X | Enum | n/a |
| Material (Opaque) | A building material (e.g. wood, concrete, steel, etc.): |  |  |  |  |
|  | Identification | X |  | String | n/a |
| Material Layer (Opaque) | An individual building layer in a material layer set: |  |  |  |  |
|  | Identification | X |  | String | n/a |
|  | Description | X |  | String | n/a |
|  | Material | X |  | String | n/a |
| Material Layer Set (Opaque) | An ordered list of material layers used in a building element construction: |  |  |  |  |
|  | Identification | X |  | String | n/a |
|  | Description | X |  |  |  |
|  | List of material layers | X |  | List of String | n/a |
| Photovoltaics | The following describes properties for PV electricity generation on-site: |  |  |  |  |
|  | Photovoltaics |  | X | Boolean |  |
|  | Host Building Element (required if 'Photovotaics' = TRUE) |  | X | Relationship | n/a |
|  | Active Area Fraction (fraction of host element with PVs) (required if 'Photovotaics' = TRUE) |  | X | Real | % |
|  | DC to AC Inverter Conversion Efficiency (required if 'Photovotaics' = TRUE) |  | X | Real | % |
|  | PV Surface Integration (Decoupled, Integrated, Integrated w/ Ventilation) (required if 'Photovotaics' = TRUE) |  | X | Enum | n/a |
|  | PV Cell Efficiency (required if 'Photovotaics' = TRUE) |  | X | Real | % |

## Exchange Requirements - Energy Analysis Inputs 2 (Mechanical Engineer/Energy Consultant)

| Type of Information | Information Needed | Required | Optional | Data Type | Units |
| --- | --- | --- | --- | --- | --- |
|  | *** NOTE: ALL INFORMATION THAT IS REQUIRED IN INPUTS 1 IS ALSO REQUIRED IN INPUTS 2. INFORMATION THAT IS OPTIONAL IN INPUTS 1 AND HIGHLIGHTED IN YELLOW IS EITHER OPTIONAL OR REQUIRED IN INPUTS 2 *** |  |  |  |  |
| Building (Energy Target) | The following properties should be included (if not known then probable values should be used): |  |  |  |  |
|  | Energy Target Units (mandatory if Energy Target Value is included) | X |  | String | varies |
|  | Energy Target Value | X |  | Real | varies |
| Spaces | The following properties should be included (if not known then probable values should be used): |  |  |  |  |
|  | Space Usage (thermal simulation type) | X |  | Enumeration value | n/a |
|  | Space Conditioning Requirement (heated and cooled, heated only, cooled only, unconditioned) | X |  | Enumeration value | n/a |
|  | Space Occupant Density | X |  | Real | People/m2 |
|  | Occupant Heat Rate | X |  | Real | Watts/ person |
|  | Space Occupant Load | X |  | Real | W/m2 |
|  | Space Lighting Load | X |  | Real | W/m2 |
|  | Space Equipment Load | X |  | Real | W/m2 |
|  | Occupancy Schedule | X |  | List of Day/Time | Calendar |
|  | Lighting Schedule | X |  | List of Day/Time | Calendar |
|  | Equipment Schedule | X |  | List of Day/Time | Calendar |
| Spaces (Thermal Comfort Criteria) | Define the temperatures required in a space for heating and cooling. The following properties should be included (if not known then probable values should be used): |  |  |  |  |
|  | Inside dry bulb temperature for cooling design | X |  | Real | °C |
|  | Inside relative humidity for cooling design | X |  | Real | % |
|  | Inside dry bulb temperature for heating design | X |  | Real | °C |
|  | Inside relative humidity for heating design | X |  | Real | % |
| Spaces (Ventilation Criteria) | Set the requirements for ventilation in a space. The following properties should be included (if not known then probable values should be used) |  |  |  |  |
|  | Indication that the space is required to have natural, mechanical ventilation, or mixed mode ventilation. | X |  | Enumeration value | n/a |
|  | Natural air change rate required for the space concerned |  | X | Real | ach |
|  | Mechanical air change rate required for the space concerned |  | X | Real | ach |
|  | Design quantity of outside air to be provided per person in the space | X |  | Real | m3/s/person |
| Spaces (Ventilation Design) | Set the results for ventilation design in a space. The following properties should be included (if not known then probable values should be used): |  |  |  |  |
|  | Air flow rate required during the peak cooling conditions |  | X | Real | m3/s |
|  | Air flow rate required during the peak heating conditions |  | X | Real | m3/s |
|  | Design exhaust air flow rate for the space. (Note that for a space that is to be under positive pressure, this value will be less than the values indicated above.) |  | X | Real | m3/s |
|  | Whether a ceiling plenum is to be used for return air or not (True/False) | X |  | Boolean | n/a |
| Building Elements (Opaque- Wall, Roof, Floor, Ceiling, Door) | Added to the list above, the following properties should be included for opaque building elements (e.g. walls, floors, ceilings, roofs, doors, etc.): |  |  |  |  |
|  | Composite Thermal Resistance | X |  | Real | m2-K/W |
| Building Elements (Glazing- Curtain Wall, Glazed Door, Skylight, Window) | Added to the Building Elements list above, assigns thermal information to building elements to enable energy analysis. The following properties should be included for glazed building elements (e.g. windows, curtain walls, glazed doors, and skylights): |  |  |  |  |
|  | Window Assembly Exterior Surface Color of Glass (clear, bronze, silver, gold, copper, blue, green, gray, mirror) |  | X | Enum | n/a |
|  | Window Assembly Interior Surface Color of Glass (clear, bronze, silver, gold, copper, blue, green, gray, mirror) |  | X | Enum | n/a |
|  | Transmittance (Visible) |  | X | Real | % |
|  | Transmittance (Solar) |  | X | Real | % |
|  | Composite U-Value |  | X | Real | W/m2-K |
|  | Shading Coefficient (SC) |  | X | Real | % |
|  | Solar Heat Gain Coefficient (SHGC) |  | X | Real | % |
|  | Manufacturer |  | X | String | n/a |
|  | Product ID |  | X | String | n/a |
| Material (Opaque) | A building material (e.g. wood, concrete, steel, etc.): |  |  |  |  |
|  | Roughness (VeryRough, Rough, MediumRough, MediumSmooth, Smooth, VerySmooth) |  | X | Enum | n/a |
|  | Density |  | X | Real | kg/m3 |
|  | Specific Heat |  | X | Real | J/kg-K |
|  | Thermal Conductivity |  | X | Real | W-m/m2-K |
| Material Layer (Opaque) | An individual building layer in a material layer set: |  |  |  |  |
|  | Thermal Resistance (not possible in binding to IFC 2x3. To be added in binding to 2x4) | X |  | Real | m2-K/W |
|  | Thickness | X |  | Real | mm |
|  | Absorptivity (Thermal) (not possible in binding to IFC 2x3. To be added in binding to 2x4) |  | X | Real | % |
|  | Absorptivity (Solar) (not possible in binding to IFC 2x3. To be added in binding to 2x4) |  | X | Real | % |
|  | Absorptivity (Visible) (not possible in binding to IFC 2x3. To be added in binding to 2x4) |  | X | Real | % |
| Energy Analysis Zones | The following properties should be included (if not known then probable values should be used). All spaces in the building must be assigned to only one thermal zone. |  |  |  |  |
|  | Identification (User facing) | X |  | String | n/a |
|  | Description |  | X | String | n/a |
|  | Zone Type (Energy Analysis) (thermal zone, plenum, other) | X |  | Enumeration value | n/a |
|  | Zone Conditioning Requirement (heated and cooled, heated only, cooled only, unconditioned) | X |  | List of Enumeration values | n/a |
|  | Member spaces (i.e. list of links) | X |  | List of Relationships | n/a |
|  | HVAC System Type (CV, VAV, Unitary, HP, Radiant, UFAD, DV, NV, MM, Other (specify)) | X |  | Enumeration value | n/a |
|  | User Defined HVAC System Type (required if HVAC System Type = "Other") |  | X | String |  |
|  | HVAC Operating Schedule | X |  | List of Day/Time | Calendar |
|  | Infiltration Rate | X |  | Real | ach |
|  | Is Daylit Zone | X |  | Boolean | n/a |
|  | Number of Daylighting Sensors (Required if Daylit = TRUE) |  | X | Integer | Count |
|  | Coordinates of each Daylighting Sensor (Required if Daylit = TRUE) |  | X | Real | m |
|  | Design Illuminance (Required if Daylit = TRUE) |  | X | Real | Lux |
|  | Lighting Controls (Continuous, Stepped, Continuous/Off) (Required if Daylit = TRUE) |  | X | List of Controls | n/a |
| Photovoltaics | The following describes properties for PV electricity generation on-site: |  |  |  |  |
|  | Photovoltaics | X |  | Boolean |  |
|  | Host Building Element (required if 'Photovotaics' = TRUE) |  | X | Relationship | n/a |
|  | Active Area Fraction (fraction of host element with PVs) (required if 'Photovotaics' = TRUE) |  | X | Real | % |
|  | DC to AC Inverter Conversion Efficiency (required if 'Photovotaics' = TRUE) |  | X | Real | % |
|  | PV Surface Integration (Decoupled, Integrated, Integrated w/ Ventilation) (required if 'Photovotaics' = TRUE) |  | X | Enum | n/a |
|  | PV Cell Efficiency (required if 'Photovotaics' = TRUE) |  | X | Real | % |

# Exchange Requirements for Energy Simulation Results

| Name | Exchange of Energy Simulation Output Results |
| --- | --- |

| Identifier | ER_EnergyAnalysis_Results |
| --- | --- |

| Change Log |
| --- |
| 15-May-08 | Initial version, adapted from Energy Analysis IDM originally developed by Jeff Wix for buildingSMART Norway | Richard See |
| 05-Jun-08 | Changes for version 0.15 | Richard See |
| 27-Aug-08 | Changes for version 0.2 | Benjamin Welle Richard See |
| 09-Sept-08 | Changes for version 0.3 | Benjamin Welle Richard See |
| 11-Sept-08 | Changes for version 0.4 | Benjamin Welle Richard See |
| 04-Dec-08 | Changes for version 0.91 | Benjamin Welle Richard See |
| 18-Jan-09 | Changes for version 0.95 | Benjamin Welle Richard See |

| Project Stage | 0 | Portfolio requirements |  |
| --- | --- | --- | --- |
|  | 1 | Conception of need |  |
|  | 2 | Outline feasibility |  |
|  | 3 | Substantive feasibility |  |
|  | 4 | Outline conceptual design | ( |
|  | 5 | Full conceptual design | ( |
|  | 6 | Coordinated design and procurement |  |
|  | 7 | Production information |  |
|  | 8 | Construction |  |
|  | 9 | Operation and maintenance |  |
|  | 10 | Disposal |  |

## Overview

The scope of this exchange requirement is the exchange of information about energy demand, comfort, and annual energy consumption. The purpose of the exchange requirement is to enable coordination of energy analysis with other design roles based on the results of energy analysis and the ability to comply with set energy targets. The exchange requirement assumes that the information provisions outlined in the exchange requirement ER_EnergyAnalysis_Inputs_2 have been satisfied.

Information that is provided by this exchange requirement to includes:

ventilation requirements

peak thermal loads

energy demand

annual energy consumption

utility rates

energy costs

## Exchange Requirements - Energy Analysis Results

| Type of Information | Information Needed | Required | Optional | Data Type | Units |
| --- | --- | --- | --- | --- | --- |
| Prerequisites | The provisions of the exchange requirements ER_EnergyAnalysis_Inputs_2 must be satisfied. | X |  |  |  |
| Project | The following properties should be included: |  |  |  |  |
|  | Identification | X |  | String | n/a |
|  | Owner/Client information |  | X | String | n/a |
| Site (Outside Design Criteria) | The following properties should be included (if not known then probable values should be used): |  |  |  |  |
|  | Outside dry bulb temperature for heating design | X |  | Real | °C |
|  | Outside wet bulb temperature for heating design | X |  | Real | °C |
|  | The month, day and time that has been selected for the heating design calculations | X |  | Date/Time | Calendar |
|  | Daily Temperature Range |  | X | Real | °C |
|  | Barometric Pressure |  | X | Integer | Pa |
|  | Sky Clearness |  | X | Real | none |
|  | Snow Indicator (0=no snow on ground, 1=snow on ground) |  | X | Boolean | n/a |
|  | Rain Indicator (0=dry surfaces, 1=wet surfaces) |  | X | Boolean | n/a |
|  | The prevailing wind angle direction measured from True North (0 degrees) in a clockwise direction during the winter | X |  | Real | Angular Degrees |
|  | The design wind velocity coming from the direction specified by the PrevailingWindDirection attribute during the winter | X |  | Real | m/s |
|  | Outside dry bulb temperature for cooling design | X |  | Real | °C |
|  | Outside wet bulb temperature for cooling design | X |  | Real | °C |
|  | The month, day and time that has been selected for the cooling design calculations | X |  | Date/Time | Calendar |
|  | Daily Temperature Range |  | X | Real | °C |
|  | Barometric Pressure |  | X | Integer | Pa |
|  | Sky Clearness |  | X | Real | none |
|  | Snow Indicator (0=no snow on ground, 1=snow on ground) |  | X | Boolean | n/a |
|  | Rain Indicator (0=dry surfaces, 1=wet surfaces) |  | X | Boolean | n/a |
|  | The prevailing wind angle direction measured from True North (0 degrees) in a clockwise direction during the summer | X |  | Real | Angular Degrees |
|  | The design wind velocity coming from the direction specified by the PrevailingWindDirection attribute during the summer | X |  | Real | m/s |
|  | The site weather data station description or reference to the data source from which weather data was obtained | X |  | String | n/a |
| Ventilation Design | Set the results for ventilation design. (Note that ventilation design may be captured for any unit of spatial structure. It is required that ventilation design will be captured for building and zones.) |  |  |  |  |
|  | Air flow rate required during the design day cooling conditions | X |  | Real | m3/s |
|  | Air flow rate required during the design day heating conditions | X |  | Real | m3/s |
|  | Exhaust air flow rate during the design day cooling conditions (Note that if the area is to be under negative pressure, this value may be the same as the air flow rates indicated above. If the area is to be under positive pressure, this value will be less than the values indicated above) | X |  | Real | m3/s |
|  | Air flow rate required during the peak cooling conditions | X |  | Real | m3/s |
|  | Air flow rate required during the peak heating conditions | X |  | Real | m3/s |
|  | Exhaust air flow rate during the peak cooling conditions (Note that if the area is to be under negative pressure, this value may be the same as the air flow rates indicated above. If the area is to be under positive pressure, this value will be less than the values indicated above) | X |  | Real | m3/s |
|  | The month, day, and time that the peak cooling ventilation requirement occurs | X |  | Date/Time | Calendar |
|  | The month, day, and time that the peak heating ventilation requirement occurs | X |  | Date/Time | Calendar |
| Peak Loads | Capture the results of peak load calculations. (Note that peak loads may be captured for any unit of spatial structure. Here, it is assumed that peak loads will be captured for the building and zones.) |  |  |  |  |
|  | The total sensible heat or energy gained during the design day cooling conditions | X |  | Real | kW |
|  | The total amount of heat or energy gained during the design day cooling conditions | X |  | Real | kW |
|  | The total amount of heat or energy lost during the design day heating conditions | X |  | Real | kW |
|  | The total people heat or energy gained (sensible/latent) during design day cooling conditions | X |  | Real | kW |
|  | The total lighting heat or energy gained (sensible) during design day cooling conditions | X |  | Real | kW |
|  | The total equipment heat or energy gained (sensible) during design day cooling conditions | X |  | Real | kW |
|  | The total envelope heat or energy gained ( sensible) during design day cooling conditions | X |  | Real | kW |
|  | The total ventilation (OA) heat or energy gained (sensible/latent) during design day cooling conditions | X |  | Real | kW |
|  | The total infiltration heat or energy gained (sensible/latent) during design day cooling conditions | X |  | Real | kW |
|  | The total sensible heat or energy gained during the peak cooling conditions | X |  | Real | kW |
|  | The total amount of heat or energy gained during the peak cooling conditions | X |  | Real | kW |
|  | The total amount of heat or energy lost during the peak heating conditions | X |  | Real | kW |
|  | The total people heat or energy gained (sensible/latent) during peak cooling conditions | X |  | Real | kW |
|  | The total lighting heat or energy gained (sensible) during peak cooling conditions | X |  | Real | kW |
|  | The total equipment heat or energy gained (sensible) during peak cooling conditions | X |  | Real | kW |
|  | The total envelope heat or energy gained ( sensible) during peak cooling conditions | X |  | Real | kW |
|  | The total ventilation (OA) heat or energy gained (sensible/latent) during peak cooling conditions | X |  | Real | kW |
|  | The total infiltration heat or energy gained (sensible/latent) during peak cooling conditions | X |  | Real | kW |
|  | The month, day, and time that the peak cooling load occurs | X |  | Date/Time | Calendar |
|  | The month, day, and time that the peak heating load occurs | X |  | Date/Time | Calendar |
| Energy Consumption | Captures the rate of energy consumption over a designated period of time for various categories of energy consumption and for total energy consumption. (Note that energy consumption may be captured for any unit of spatial structure. Here, it is assumed that energy consumption will be captured for the building and zones.) |  |  |  |  |
|  | The unit period of time in which energy consumption is measured (per month, per year, etc.) | X |  | Enumeration value | n/a |
|  | The amount of energy consumed for heating purposes during the time period specified | X |  | Real | kWh |
|  | The amount of energy consumed for cooling purposes during the time period specified | X |  | Real | kWh |
|  | The amount of energy consumed for lighting purposes during the time period specified | X |  | Real | kWh |
|  | The amount of energy consumed for equipment (plug load) purposes during the time period specified | X |  | Real | kWh |
|  | The amount of energy consumed for other (other than heating, cooling, lighting and equipment) purposes during the time period specified | X |  | Real | kWh |
|  | The total amount of energy consumed for all purposes during the time period specified | X |  | Real | kWh |
| Thermal Comfort | Captures the number of annual operating hours at the building and zone level that the design conditioning requirements cannot be met. |  |  |  |  |
|  | Number of hours design cooling requirements cannot be met | X |  | Real | hours |
|  | Number of hours design heating requirements cannot be met | X |  | Real | hours |
| Energy Tariff | Cost values that apply to the source of energy and its form of usage. (During the early stages of design, information may be obtained from similar projects. As design progresses, information is obtained from the energy source provider. Multiple energy tariffs may be defined based on project needs. Energy and demand charges may apply.) |  |  |  |  |
|  | Energy Source (Electricity, Gas, Propone, Other) | X |  | Enumeration value | n/a |
|  | Energy Tariff Unit (kWh, kW, therm, etc.) | X |  | Enumeration value | varies |
|  | Cost value to be applied | X |  | Real | $/unit |
|  | Identification that the cost value is an energy tariff (True/False) | X |  | Boolean | n/a |
|  | Time series applicability of the energy tariff (The tariff may be applicable not only to the energy source but also to when the energy source is used. For instance, electrical energy may carry a lower tariff when it is used in 'off peak' situations since such this may be useful to the source provider in load balancing.) Options are “summer peak, summer shoulder, summer offpeak, winter peak, winter shoulder, winter offpeak) | X |  | List of Day/Time | Calendar |
| Energy Costs | Captures the annual energy costs at the building level. |  |  |  |  |
|  | Annual Electricity Costs | X |  | Real | $/yr |
|  | Annual Gas Costs | X |  | Real | $/yr |
|  | Annual Fuel Costs (Other) | X |  | Real | $/yr |
|  | Peak Demand Charge | X |  | Real | $/month |
|  | Month of Peak Demand | X |  | String | n/a |
|  | Photovoltaic Energy Delivered (required if 'Photovotaics' = TRUE) |  | X | Real | kWh/yr |

# Comments

Field is meant only for project identifier. Field a text or a number.

Address includes street address, city, state, and country.

This field is required. Latitude and longitude are required. Site may have several buildings.  Reference point is building model origin of the BIM (top level container).

Grid orientation is assumed to be zero degrees -- that is: Y axis points true north

3D Geometry under Site category refers to 3D modeling of site terrain.

Site context refers to information about surrounding buildings, i.e. shells of adjacent buildings.

This is numerical or text field.

This field is required. Lattitude and longitude are required. A single building could have many different referece points. Building origin (container) referenced to the site origin (container).

Changed to align with QTO Thread.

Building orientation is typically considered to be the degrees of grid rotation from true north. Building orientation specification, therefore, is somewhat arbitrary for the building could have been modeled in any particular orientation on the original grid.  Determining the direction of the surface normals is the critical component.

Base elevation of ground level floor above sea level.

Different possible metrics here: Btu/ft2, kWh/person, kWh/ft2 cooling, kWh/ft2 heating, kWh/ft2 by end use, etc.  Targets may be based on ASHRAE 90.1, state or local codes, LEED requirements/goals, etc.

This is numerical or text field.

This must include both Space Number and Space Name

Space name or number…1,2, mezzanine, etc.

Optional text description.

Space classification is specific to the client/profile.  They may or may not have spatial naming conventions to follow.  Example: GSA Star Space Type. Will be required for the GSA.

Richard, we want to allow for multiple classifications here.  Once mappings are complete between IBC, IEEC, Omniclass, GSA Star Space Type, etc. we may want to include several of these.

Optional for Architect (EA_Input_1), mandatory for Engineer (EA_Input_2)

Cannot always be derived from 3D geometry.

The same space could be assigned to two different zones (HVAC and non-HVAC). If a space is assigned to two conditioned zones, must divide space. We will require that spaces can only be assigned to one HVAC zone.

Optional for Architect (EA_Input_1), mandatory for Engineer (EA_Input_2)

Architect should declare the material and material Layer

Same comment …

We will use symmetric layers for interior walls.  Standard of layer sequencing is from outside to inside.

Different possible metrics here: Btu/ft2, kWh/person, kWh/ft2 cooling, kWh/ft2 heating, kWh/ft2 by end use, etc.  Targets may be based on ASHRAE 90.1, state or local codes, LEED requirements/goals, etc.

Space type: Office, hallway, storage, etc. Used to determine load assumptions. Does not need to match space classification. Should use accepted standard such as OMNICLASS to determine space types.

Table 13 Omniclass on option. Can then use mapping table for EP.

Can use to drive assumptions in IDF editor.

Include plenums as a space type.

The same space could be assigned to two different zones (HVAC and non-HVAC). If a space is assigned to two conditioned zones, must divide space. We will require that spaces can only be assigned to one HVAC zone.

Container referencing the objects- GST assumes non-assigned spaces are unconditioned.

Zones objects in IFC do not have geometry themselves

Name or number.

Text description.

Conditioned vs. unconditioned.  There may be a conflict between zone conditioning requirement and space conditioning requirements of the associated spaces. This must be tagged as an error.

IFC zone objects will become thermal zones in EnergyPlus under current process structure.

Peaks for building, zone, and space may occur at different times, which is why it is required to specify peaks for each level. Additionally, data is required for both design day and peak load. Peak loads may not coincide with the design day.

When spaces are aggregated into zones for conversion to EnergyPlus or DOE2 thermal zones, output results are only available for the aggregated “zone” objects.  GST removes all the internal walls from contiguous rooms in a zone, and models all the spaces as one large space.  Consequently, data on the spatial level will not be available in these situations.  When a space is considered its own thermal zone, then spatial data will be available.

There is an option to keep internal walls, but still assign multiple spaces, even non-contiguous, to a single zone object.